**CVPCSD Monthly Report**

January 2024

Daily average flow = 175 gpm

Daily Average Raw NTU = 4.28

Daily Average Finished NTU = 0.026

**Water Plant –**

* **Putting supplies together for SCC pump install**
* **Found leak at booster pump manifold. Have parts to repair. Holding off to see if we move forward with Hydros proposal.**
* **Cleaning around basin for blackberries.**
* **Had some “sheen” on the first two floc basins after canal cleaning. We have been monitoring and whenever we see it, we have thrown straw down and removed. Have not seen anything for a about a week as of this report. If we see it again, I will take a sample. We have had absorbent “dams” to keep it isolated.**
* **New Compressor for Air system.**

**Distribution –**

* Repaired Gayle lane service (Diane). Paving to be completed.
* Multiple curb stops scheduled to be repaired. Lorang excavated prior.
* Leak at 3” manifold service on Marry lane. Had to shut down 70 services. All wfas repaired properly. It was found that the joints were never glued when installed. Sampled main and all houses effected on repair.

**Summary**

* State inspection scheduled for Feb 15th.
* PCARCB inspection scheduled for Deb 9th
* Need to look into some sort of notification alert software.
* Need to do an audit of the district for customer contact info.